Appendix A Specification of Requirements

Contents

1.	Objective	2

2.	Conditions	2

3.	General	2

4.	GenerAl requirements	2

5.	SpecifIc requirements	3

5.1	Energy and power	4

5.2	Ventilation	6

5.3	Indoor climate	8

5.4	Design and installation	13

5.5	Operation and Maintenance	17

5.6	Robustness	21

5.7	Cost reporting	24

5.8	The Tenderer	25

- Objective

The aim of this Technology Competition is to stimulate a market-driven development of integrated heating and ventilation solutions for single-family detached houses. The solutions are to be designed for existing houses with electric resistance heating and natural ventilation. The goal is also for these novel solutions to be cost efficient and energy efficient, and that the solutions shall be made available on the Swedish market. The solution is hereinafter referred to as the system.

- Conditions

This technology competition involves the development of an integrated heating and ventilation system. The system shall be adapted for existing detached single-family houses with electric resistance heating and natural ventilation. The system has to be suitable for being used in a Nordic climate, and must function throughout the year under all ambient outdoor temperature conditions. The best system(s) proposed in this technology competition are expected to be used in detached single-family houses in Sweden, and will be tested in demonstration houses as described in Appendix B of the tender documents.

This specification of requirements includes a complete heating and ventilation system as follows:

- a full system for heating and ventilation including all necessary components (e.g. radiators, pipes, ducts, pipe and duct insulation, duct silencers, combination roof terminal, supply air diffusers, fire dampers, thermostatic valves),

- installation of the system and any additional measures required during installation (e.g. sealing of the building envelope, construction of mechanical rooms, balancing of heating and ventilation systems, restoration of surface finishes),

- commissioning and performance monitoring of the system during the first year of operation.

- General

The requirements of the technology competition are formulated as mandatory requirements and desired requirements. All mandatory requirements must be fulfilled for the submission to be considered for the next phase of the competition. Fulfilment of desired requirements is optional, and will be evaluated through a scoring system.

When the technology competition is announced, the tenderer must mark the corresponding box for each of the requirements that is fulfilled and provide a written explanation in accordance with the instructions in this requirement specification.

- GenerAl requirements

In this chapter the general requirements for the technology competition are described.

- Functionality

  - The system must provide heating and ventilation for the entire demonstration single-family house.

  - The system must replace the existing electric resistance heating system in the demonstration house.

  - The system must replace the existing natural ventilation system in the demonstration house.

- Legislation

In addition to the specific requirements stated in this specification, the system must comply with all applicable laws and regulations in the country of implementation. For installations in Sweden, the following apply in particular:

  - Regulatory requirements for building alterations, e.g. conservation, accessibility, fire safety, etc.

  - Building codes, safety regulations, and data protection law

  - All functional requirements in the Swedish National Board of Housing, Building and Planning’s Building Regulations (BBR, current version) concerning energy efficiency, control, and smart technology for new detached single-family houses

  - General guidelines from the Public Health Agency of Sweden regarding indoor temperatures, ventilation, indoor noise, moisture, and microorganisms

  - EU Ecodesign Directive

  - EU Machinery Directive and Machinery Regulation

- User-friendliness

  - The system must be accessible for use by homeowners without prior knowledge of control and monitoring systems for technical installations.

- Cost reporting

  - Cost reporting must be done using the template provided in Appendix C of the tender documents (LCC calculation template).

- Warranties

- Warranties for both hardware and software offered for 5 years are mandatory and are desired to be offered for 10 years.

- Contract

- For the demonstration phase of the competition, a contract will be established between the owner of the demonstration house (private individual) and the main contractor, for example using the “Hantverkarformulär 17” (Craftsman Form 17).

- SpecifIc requirements

In column “Parameter” in the Table below, the requirements formulated by the reference group associated with this technology competition are presented. Columns 2 and 3 show whether the current requirement is a “mandatory” requirement (must be met) or a “desired” requirement (is meritorious).

The two right-hand columns state how verification of compliance with the requirements will take place during the tender evaluation and after installation of the system, respectively. For each individual requirement, the tenderer must describe how the requirement is met. Please note that the tenderer must report all input data and calculation methods so that the committee and jury of the technology competition can review and assess the tender responses.

Energy and power

| Parameter | Requirement |  | Verification |  |  |  |  | Answer to the Request for Information |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Mandatory | Desired |  |  | Evaluation step 1 | Evaluation step 2 | This field provides space for comments regarding the specific requirements. Please write only in this column. Please send this document to behovsagarnatverk@chalmersindustriteknik.se. |  |
| 5.1.1 Reduction of purchased energy |  |  |  |  |  |  |  |  |  |
| The system must contribute to a more efficient energy use in the house. Reduction of purchased energy for heating and ventilation, where the initial value is stated for the demonstration house | 60 % | 80 % |  |  | Reviewed and evaluated by the committee | On-site measurements in the demonstration house. Evaluated for an indoor temperature of 21°C. | Comment: Write text here |  |
| 5.1.2 Energy monitoring, demonstration |  |  |  |  |  |  |  |  |  |
| The system has an energy monitor, with digital logging and transfer of the data | Must be fulfilled for the demonstration house |  |  | Reviewed and evaluated by the committee |  | Testing of functionality in the demonstration house | Comment: Write text here |  |
| 5.1.3 Built-in energy monitor, final product |  |  |  |  |  |  |  |  |  |
| The system has a built-in energy monitor, with digital logging and transfer of the data |  | Desired to be fulfilled for systems made accessible on the Swedish market |  | Reviewed and evaluated by the committee |  |  | Comment: Write text here |  |
| 5.1.4 Power demand, heating |  |  |  |  |  |  |  |  |  |
| Reduction of maximum power requirement for heating. Hourly average power, reported at -7°C where the starting value is given for demonstration houses. | 50 % | 70 % |  | Reviewed and evaluated by the committee |  | On-site measurements in the demonstration house, as well as evaluation using power signatures | Comment: Write text here |  |
| 5.1.5 Energy requirement, domestic hot water |  |  |  |  |  |  |  |  |  |
| The system has integrated hot water production which reduces purchased energy for heating, ventilation and hot water, where the starting value is given for a demonstration house. |  | 70 % |  | Reviewed and evaluated by the committee |  | On-site measurements in the demonstration house | Comment: Write text here |  |

Ventilation

| Parameter | Requirement |  |  |  |  | Verification |  | Answer to the Request for Information |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Mandatory |  |  |  | Desired | Evaluation step 1 | Evaluation step 2 |  |
| 5.2.1 Ventilation air flows |  |  |  |  |  |  |  |  |
| Ventilation air flows must be minimum 0,35 l/s/m2 | Must be fulfilled |  |  |  |  | Presentation including calculations and a sketch are reviewed and evaluated by the committee | On-site measurements in the demonstration house | Comment: Write text here |
| 5.2.2 Air distribution |  |  |  |  |  |  |  |  |
| The air distribution from the ventilation system must be satisfactory so that an air change equivalent of 0.5 ACH is achieved for all rooms in the house (occupancy zones). | Must be fulfilled |  |  |  |  | Reviewed and evaluated by the committee | On-site measurements in the demonstration house with CO2-measurements in each occupancy zone | Comment: Write text here |
| 5.2.3 Ventilation air flows, no occupancy |  |  |  |  |  |  |  |  |
| The ventilation airflows with no occupancy can be reduced centrally to 0.2 l/s/m2 |  |  |  | Desired to be fulfilled |  | Reviewed and evaluated by the committee | Testing of functionality in the demonstration house | Comment: Write text here |
| 5.2.4 Air intake and air outlet |  |  |  |  |  |  |  |  |
| Short circuiting between outside air at air intake and exhaust air must not occur. | Solution for air intake and air outlet must be presented in a sketch with dimensions and location. |  |  |  |  | Reviewed and evaluated by the committee | Visual inspection on-site in the demonstration house | Comment: Write text here |

Indoor climate

| Parameter | Requirement |  |  | Verification |  | Answer to the Request for Information |
| --- | --- | --- | --- | --- | --- | --- |
|  | Mandatory | Desired | Evaluation step 1 |  | Evaluation step 2 |  |
| 5.3.1 Sound and vibration noise |  |  |  |  |  |  |
| 5.3.1a Sound pressure level from the heating and ventilation system does not exceed requirements according to BFS 2024:10 in the occupied zone | Must be fulfilled |  | Reviewed and evaluated by the committee |  | Verified by on-site measurements in the demonstration house | Comment: Write text here |
| 5.3.1b Outdoor noise level does not exceed requirements in accordance with the Ecodesign Regulation | Provide a description of how the system will be implemented under different installation conditions so that the free-field normalized sound pressure at the plot boundary does not exceed 40 dBA |  | Reviewed and evaluated by the committee |  | Verified by on-site measurements in the demonstration house | Comment: Write text here |
| 5.3.1c Vibration noise | Provide a description of how vibration noise from the system is mitigated |  | Reviewed and evaluated by the committee and the jury |  | Reviewed and evaluated on-site in the demonstration house | Comment: Write text here |
| 5.3.2 Draft in the occupied zone |  |  |  |  |  |  |
| Draft from the ventilation system in the occupied zone | Draft from the ventilation system in the occupied zone must not exceed 0.15 m/s during the heating season. |  | Reviewed and evaluated by the committee and the jury |  | Verified by on-site measurements in the demonstration house | Comment: Write text here |
| 5.3.3 Down draft |  |  |  |  |  |  |
| Avoid risks for problems related to moisture and health issues | If the proposed solution results in increased down drafts from the windows, a compensating measure must be presented to ensure that risks related to moisture and health issues are avoided |  | Reviewed and evaluated by the committee and the jury |  | Verified by moisture and down draft measurements on-site in the demonstration house | Comment: Write text here |
| 5.3.4 Indoor temperatures during occupancy |  |  |  |  |  |  |
| Indoor temperatures during occupancy in winter | The indoor temperature during occupancy in winter must be 21±3°C |  | Reviewed and evaluated by the committee |  | Verified by on-site measurements in the demonstration house | Comment: Write text here |
| 5.3.5 Integrated cooling function |  |  |  |  |  |  |
| Function for integrated cooling in the bedroom during summer |  | The system is desired to have an integrated cooling function that helps ensure the bedroom temperature does not exceed 26 °C during summer | Reviewed and evaluated by the committee and the jury |  |  | Comment: Write text here |
| 5.3.6 Supply air temperature |  |  |  |  |  |  |
| Supply air temperature of the ventilation system | The ventilation system supply air temperature must not exceed 52 °C |  | Reviewed and evaluated by the committee |  | Verified by on-site measurements and evaluation in the demonstration house | Comment: Write text here |
| 5.3.7 Air quality |  |  |  |  |  |  |
| 5.3.7a Air filter supply air | Air filters corresponding to the filter classes according to ISO 16890 must be used for the supply air (ePM1 50 %- filter) |  | Reviewed and evaluated by the committee |  | On-site inspection in the demonstration house | Comment: Write text here |
| 5.3.7b Air filter supply air |  | The supply air filters are desired to be replaceable with ePM1 70 %-filter | Reviewed and evaluated by the committee |  | On-site inspection in the demonstration house | Comment: Write text here |
| 5.3.7c Testing of air filters according to Eurovent 4/22 |  | All air filters are desired to be tested according to Eurovent 4/22 | Reviewed and evaluated by the committee and the jury |  | On-site inspection in the demonstration house | Comment: Write text here |

Design and installation

| Parameter | Requirement |  | Verification |  | Answer to the Request for Information |
| --- | --- | --- | --- | --- | --- |
|  | Mandatory | Desired | Evaluation step 1 | Evaluation step 2 |  |
| 5.4.1 Integration of existing ducts |  |  |  |  |  |
| The system makes use of existing ventilation ducts, if available |  | The system is desired to make use of existing ventilation ducts, if available | Reviewed and evaluated by the committee and the jury | On-site verification in the demonstration house | Comment: Write text here |
| 5.4.2 Aesthetic design of visible components |  |  |  |  |  |
| Components and devices that will be visible in the system shall be aesthetically pleasing | The design of all visible components must be reported and must include supporting images or drawings |  | Reviewed and evaluated by the committee and the jury | On-site inspection in the demonstration house | Comment: Write text here |
| 5.4.3 Space for equipment |  |  |  |  |  |
| Space requirements for the system | The area required for equipment located indoors (in warm and cold spaces) and outdoors must be presented in a drawing including dimensions |  | The committee and jury will review and evaluate the system’s encroachment on the usable floor area of the house | On-site verification in the demonstration house through control measurements | Comment: Write text here |
| 5.4.4 Size |  |  |  |  |  |
| 5.4.4a Maximum width of the indoor system (reducing usable floor area) | The width must not exceed 1.2 m |  | Reviewed and evaluated by the committee | On-site verification in the demonstration house through control measurements | Comment: Write text here |
| 5.4.4b Maximum depth of the indoor system (reducing usable floor area) | The depth must not exceed 0,6 m |  | Reviewed and evaluated by the committee | On-site verification in the demonstration house through control measurements | Comment: Write text here |
| 5.4.4c Maximum height of the indoor system (reducing usable floor area) | The height must not exceed 2,0 m |  | Reviewed and evaluated by the committee | On-site verification in the demonstration house through control measurements | Comment: Write text here |
| 5.4.5 Control system |  |  |  |  |  |
| 5.4.5a Temperature control | The system’s control system must include temperature control within the comfort range (21±3°C) during occupancy |  | Reviewed and evaluated by the committee and the jury | On-site verification in the demonstration house through functional inspection | Comment: Write text here |
| 5.4.5b Temperature control |  | The system’s control system includes control of indoor temperatures in different rooms | Reviewed and evaluated by the committee and the jury | On-site verification in the demonstration house through functional inspection | Comment: Write text here |
| 5.4.5c Temperature control |  | The system’s control system includes a setback function that lowers the indoor temperature outside the comfort range (21 ± 3 °C) during no occupancy | Reviewed and evaluated by the committee and the jury | On-site verification in the demonstration house through functional inspection | Comment: Write text here |
| 5.4.5d Airflow control |  | The system’s control system includes centralized control of the airflows | Reviewed and evaluated by the committee and the jury | On-site verification in the demonstration house through functional inspection | Comment: Write text here |
| 5.4.5e Smart control |  | The system’s control system is desired to include smart features beyond basic functionality (e.g., alarms, fault diagnostics, Wi-Fi connectivity, and maintenance indicators) | Reviewed and evaluated by the committee and the jury | On-site verification in the demonstration house through functional inspection | Comment: Write text here |

Operation and Maintenance

| Parameter | Requirement |  | Verification |  | Answer to the Request for Information |
| --- | --- | --- | --- | --- | --- |
|  | Mandatory | Desired | Evaluation step 1 | Evaluation step 2 |  |
| 5.5.1 Operation- and maintenance instructions |  |  |  |  |  |
| 5.5.1a Operation and maintenance instructions | Operation and maintenance instructions, including cleaning, component replacements, and user guidelines (e.g., filter changes, temperature settings), must be provided in Swedish. The instructions must be clear and easily accessible throughout the system’s declared service life according to section 5.7.2. A description of how these instructions will be made available to current and future occupants must be provided. |  | Reviewed and evaluated by the committee and the jury | Reviewed and evaluated by the committee and the jury | Comment: Write text here |
| 5.5.1b Operation and maintenance instructions |  | English-language version of the operation and maintenance instructions | Reviewed and evaluated by the committee | Reviewed and evaluated by the committee | Comment: Write text here |
| 5.5.2 System walkthrough and demonstration |  |  |  |  |  |
| A system walkthrough with the occupants is conducted during the installation phase, covering how the system should be operated, maintained, and cleaned | Presentation of the walkthrough plan |  | Reviewed and evaluated by the committee | Walkthrough and demonstration conducted | Comment: Write text here |
| 5.5.3 Accessibility |  |  |  |  |  |
| The system must be accessible for service and maintenance | Accessibility must be described |  | Reviewed and evaluated by the committee | On-site verification in the demonstration house through accessibility inspection | Comment: Write text here |
| 5.5.4 System operational reliability |  |  |  |  |  |
| 5.5.4a Description of how emergency actions for system function will be carried out within Sweden | The procedure for emergency measures for system function must be described in Swedish |  | Reviewed and evaluated by the committee | Inspection of description on-site in the demonstration house | Comment: Write text here |
| 5.5.4b Description of how emergency actions for system function will be carried out within Sweden |  | The procedure for emergency measures for system function is desired to also be described in English | Reviewed and evaluated by the committee | Inspection of description on-site in the demonstration house | Comment: Write text here |
| 5.5.5 Replaceability |  |  |  |  |  |
| 5.5.5a Replacement of wear parts during the system’s declared service life according to section 5.7.2 | Wear parts that need to be replaced during the system’s declared service life must be easily replaceable. A description of how this is to be carried out must be provided in Swedish. |  | Reviewed and evaluated by the committee | Inspection of description on-site in the demonstration house | Comment: Write text here |
| 5.5.5b Replacement of wear parts during the system’s declared service life according to section 5.7.2 |  | Wear parts that need to be replaced during the system’s declared service life are desired to be easily replaceable. A description of how this is to be carried out should also be provided in English. | Reviewed and evaluated by the committee | Inspection of description on-site in the demonstration house | Comment: Write text here |
| 5.5.5c Availability of wear and spare parts | Wear and spare parts must be available throughout the system’s declared service life according to section 5.7.2. Their availability must be documented. |  | Reviewed and evaluated by the committee |  | Comment: Write text here |

Robustness

| Parameter | Requirement |  | Verification |  |  |  |  | Answer to the Request for Information |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Mandatory | Desired |  | Evaluation step 1 |  | Evaluation step 2 |  |  |  |
| 5.6.1 Maintained level of energy efficiency |  |  |  |  |  |  |  |  |  |
| The system must maintain its energy efficiency over time | The system’s energy efficiency must not decrease by more than 7 % over a period of 10 years |  | Reviewed and evaluated by the committee and the jury |  | Evaluation of submitted documentation |  | Comment: Write text here |  |
| 5.6.2 Material choice |  |  |  |  |  |  |  |  |  |
| 5.6.2a Recycled material |  | The system is desired to consist of at least 40 percent recycled material by weight | Reviewed and evaluated by the committee |  |  |  | Comment: Write text here |  |
| 5.6.2b Recycled material |  | The system is desired to consist of at least 60 percent recycled material by weight | Reviewed and evaluated by the committee |  |  |  | Comment: Write text here |  |
| 5.6.2c Recycling of material at end of life | Presentation of how the materials used in the system can be recycled (material recycling) |  | Reviewed and evaluated by the committee |  |  |  | Comment: Write text here |  |
| 5.6.2d Reuse of material |  | Presentation of how the materials used in the system can be reused | Reviewed and evaluated by the committee |  |  |  | Comment: Write text here |  |
| 5.6.2d The system must be free of substances identified as risk-reduction or phase-out substances in the Swedish Chemicals Agency (Kemikalie-inspektionen) PRIO tool | A presentation must be provided on how compliance with the requirement to exclude these substances will be ensured |  | Reviewed and evaluated by the committee and the jury |  |  |  | Comment: Write text here |  |
| 5.6.3 Refrigerants |  |  |  |  |  |  |  |  |  |
| The system must not use refrigerants subject to phase-out under the F-Gas Regulation and is as climate- and environmentally friendly as possible | A description of the refrigerants used in the system |  | Reviewed by the committee |  | On-site verification in demonstration house |  | Comment: Write text here |  |

Cost reporting

| Parameter | Requirement |  | Verification |  | Answer to the Request for Information |
| --- | --- | --- | --- | --- | --- |
|  | Mandatory | Desired | Evaluation step 1 | Evaluation step 2 |  |
| 5.7 Cost |  |  |  |  |  |
| 5.7.1a Total cost for a turnkey system | The total cost for the turnkey system must be reported |  | Reviewed and evaluated by the committee |  | Comment: Write text here |
| 5.7.1b Labor costs for installation, including any additional measures required during installation (see section 2, Conditions) | The labor cost for the installation must be reported separately |  | Reviewed and evaluated by the committee |  | Comment: Write text here |
| 5.7.2 Service life |  |  |  |  |  |
| Technical service life | Must be reported |  | A report on the technical service life of the system and its constituent components must be provided. The reported information will be reviewed and evaluated by the committee. |  | Comment: Write text here |

The Tenderer

| Parameter | Requirement |  | Verification |  | Answer to the Request for Information |
| --- | --- | --- | --- | --- | --- |
|  | Mandatory | Desired | Evaluation step 1 | Evaluation step 2 |  |
| 5.8.1 Economic and financial capacity |  |  |  |  |  |
| Economic status and financial capacity | Must be reported via extracts from allabolag.se or equivalent information for all companies included in the submission |  | Reviewed and evaluated by the committee |  | Comment: Write text here |
| 5.8.2 Capacity |  |  |  |  |  |
| The tenderer must demonstrate adequate capacity to supply the offered system to the market | Must be reported |  | Reviewed and evaluated by the committee |  | Comment: Write text here |
| 5.8.3 Experience |  |  |  |  |  |
| Relevant reference project | At least one reference project per company included in the submission must be provided |  | Reviewed and evaluated by the committee |  | Comment: Write text here |
| 5.8.4 Organization |  |  |  |  |  |
| Organizations and key personnel | The tenderer must describe the organizations and key personnel who will be involved in the demonstration project |  | Reviewed and evaluated by the committee |  | Comment: Write text here |
| 5.8.5 Quality- and environmental management system |  |  |  |  |  |
| Quality and environmental management system | The tenderer must provide a description of the quality and environmental management system implemented within each company included in the tender |  | Reviewed and evaluated by the committee |  | Comment: Write text here |
| 5.8.6 Presentation of submission |  |  |  |  |  |
| Oral presentation of the submission during the evaluation phase | The tenderer must be available to participate in an oral presentation (in Swedish or English) of the submission during the evaluation phase |  | Meeting with the tenderer |  | Comment: Write text here |

Occupancy is defined as the time when the user arrives at home.

Eurovent 4/22: Industry Recommendation for Residential Air Filter Performance Measurements - Eurovent